## Flowtests
City:
|  | Formula: Q=(29.83(C(d2)p0.5)) | [5 empty] | Formula: AFF=Q(((S-20)0.54/((S-R)0.54)))
Test No. | Location | Q (total gallons flowing) | 29.83 | Coefficient C = .9 | diameter (d) of outlet flowed in inches | Number of outlets flowing | Pitot (p) | Available Fire Flow (AFF) | Total Gallons Flowing | Static (S) | Residual (R) | Test Date | Witnessed By
1 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
2 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
3 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
4 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
5 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
6 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
7 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
8 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
9 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
10 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
11 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
12 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
13 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
14 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
15 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
16 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
17 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
18 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
19 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
20 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
21 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
22 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
23 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
24 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
25 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
26 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
27 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
28 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
29 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0
30 |  | 0 | 29.83 | 0.9 | 2.5 | 1 |  | - | 0

## How to Use the Spreadsheet
Some cells are protected to prevent the formulas from being changed by accident. To change any protected cell simply go to the Review tab and select "Unprotect Sheet." There is no password.
The values for coefficient, diameter of outlet, and number of outlets flowing are set to typical defaults but may be changed by the user as required.
For each flow test, enter the location, pitot pressure, static pressure, residual pressure, test date, and witness name. The spreadsheet will calculate the total gallons flowing (Q) and the available fire flow at 20 psi residual pressure.
Save the spreadsheet to document your flow tests.

## Read Me
Note: The worksheet is protected to help keep the formulas from being changed, but there is no password. To edit the spreadsheet, go to the Review tab in the ribbon bar and select Unprotect Sheet. To add rows to the spreadsheet, simply unprotect the sheet and copy the formulas to additional rows.
The "Q" formula [Q=(29.83(C(d2)p0.5))] is used by ISO and others to calculate water flowing during a flow test.
The Hazen-Williams formula [Available Fire Flow=Q(((S-20)0.54/((S-R)0.54)))] is used by ISO and others to determine the available fire flow at 20 psi residual pressure.
The user needs four pieces of data to use this spreadsheet: the static pressure, the residual pressure, the pitot pressure, and the sixe of the opening flowing. Generally, the 2.5" opening is used during a flowtest. Enter this information in the spreadsheet and the spreadsheet will calculate total gallons flowing during the test and the available fire flow at 20 psi residual pressure. Enter the address for documentation purposes. The spreadsheet lets you save test results for later reference.
Coefficient refers to the factor used for the type of opening in the fire hydrant inside the barrel. Most fire hydrants have a rounded opening where the outlet and barrel join. Such hydrants have a coefficient of 0.9. Hydrants with square outlets have a coefficient of 0.8. Hydrants with a square outlet that projects into the barrel have a coefficient of 0.7. Feel inside the opening and use the correct coefficient for the hydrant being flowed. These coefficients are valid for hydrant outlets of less than 4 inches. The spreadsheet does not make calculation adjustments for using the pumper outlet for the flowtest. Refer to NFPA 291, Recommended Practice for Fire Flow Testing and Marking of Hydrants for more information.

## Credit for Hydrants
ITEM 621 - CREDIT FOR HYDRANTS (CH)
Item | Description of hydrant | Number of hydrants | Points | Score
620 A. | 6-inch or larger branch and a pumper outlet, with or without 2.5" outlets; or with a 6 inch or larger dry hydrant installed in accordance with the general criteria of the applicable standard | 0 | 100 | 0
620 B. | 6-inch or larger branch, no pumper outlet, but with two or more 2.5" outlets, or with small foot valve, or with a barrel less than 5 inches in diameter | 0 | 75 | 0
620 C. | With only one 2.5" outlet | 0 | 25 | 0
620 D. | With less than a 6-inch branch | 0 | 25 | 0
620 E. | Flush type (flush or ground level) | 0 | 25 | 0
620 F. | Cistern or suction point | 0 | 25 | 0
| TOTAL | 0 |  | 0
| Credit for hydrants (CH) [Maximum out of 3 points] |  |  | 0
This spreadsheet will calculate the credit available from ISO for the number and type of fire hydrants in your community. Enter the number of each type of hydrant in the blue cells. Refer to Section 620 in the ISO Fire Suppression Rating Schedule for complete details on the types of fire hydrants eligible for credit.